Location Safety Committee - Meeting Notes
Date: October 19, 2026
Time:  1:00 PM
Location: Zoom



Attendees:
· William Wann
· Margaret Lednicky
· Erika Wescoatt
· Koue Vang
· Arthur Jenkins
· Adrienne Andrews
· Amanda James

1. McClellan Fire Alarm Response
· The committee revisited the spring incident involving smoke in the building and questions about whether the alarm system automatically notified the fire department.
· Margaret initially shared information about a separate alarm triggered during a recent fire alarm panel upgrade. William clarified that this was a different incident.
· Detection thresholds and the notification process for the spring incident remain unconfirmed.
· Margaret will clarify how the system functioned during that incident and report back to the committee.
· The discussion reiterated the importance of clear emergency contacts and fire department authorization before reoccupying an evacuated building.
2. HVAC Concerns
CTE
· Facilities Management adjusted the system to begin cooling earlier and increase conditioned airflow to affected rooms.
· Room temperatures were being monitored to evaluate effectiveness.
· Erika reported no additional complaints since the adjustments. The department submitted a work order indicating it had not experienced further issues.
STEM
· Erika reported approximately three weeks of inconsistent temperatures and negative building pressure.
· Reported effects included hot and cold areas, sewer-like odors in the mailroom, and pressure interfering with ADA door operation.
· Technicians have been manually adjusting temperature and pressure as an interim measure.
· Margaret reported that an intermittent supply fan issue in a main air handler had been diagnosed. A replacement electrical component was being sourced, with repair previously targeted for Friday. Completion had not been confirmed.
· Communication delays between building controls were also contributing to inconsistent temperatures. Required parts and technical support were being coordinated.
· No new STEM complaints or work orders had been received that day, but resolution was not confirmed.
3. Phone System Updates
· Updates requested from Minh on outstanding phone system items dating back to April remain pending.
· Koue will follow up and share the information with the committee.
4. Davies Hall Parking and Lighting
· William raised faculty concerns about lighting in alternative parking areas and along routes to workspaces when the Davies Hall parking lot closes.
· Specific locations of concern had not yet been identified.
· Koue confirmed that parking and lighting concerns will be discussed at the October 27 Operations Council meeting.
· Closure timing and alternative parking information will be shared through Admin Bites.
· Koue will raise the request for prominent website information at the following day’s Cabinet meeting and coordinate with the Public Information Office.
5. Administration Building Restroom
· Adrienne requested an update on the damaged stall in the Administration Building women’s restroom.
· Erika will obtain a repair status update from Facilities.
6. Facilities and Construction Updates
· Child Development Center shade structures: Concrete work for Shade 1 is complete, and height adjustments are underway. Shade 2 excavation is on hold pending a construction change directive showing revised post foundation locations. Completion is targeted for the end of November.
· Softball scoreboard replacement: The project is awaiting issuance of the purchase order before Beeline Sports can begin work.
· Baseball and tennis project: Draft working drawings were expected. Margaret noted that the available update was from earlier in the month and she had not yet seen the drawings.
· CTE Automotive hazardous storage: The purchase order has been issued, and the feasibility study is underway. A site meeting with the architect and stakeholders was held to review storage location options.
· Athletic snack bar feasibility studies: Soccer and PE Building studies are complete. Baseball and stadium studies are next.
· Natomas STEAM: Warranty items remain underway. LEED Silver certification was reported.
· Tech Ed modernization: Warranty items and HVAC design concerns remain ongoing. Margaret anticipates a more detailed update next month.
· New Davies Hall: The recent furniture meeting focused on offices. The November meeting will address classroom furniture. Adjustments can still be considered.
· Veterans Resource Center: Construction continues. Occupancy remains anticipated for late spring or early summer 2027.
7. Davies Hall Communications and Celebration
· Additional Davies Hall updates will be shared through Operations Council and Admin Bites.
· A celebration before demolition is being discussed.
· Academic Senate will help identify a suitable date before faculty leave for summer.
Follow-Up Items
· Margaret: Verify the spring McClellan incident’s detection and fire department notification process and share findings. Follow-up was targeted for October 20.
· Margaret/Facilities Management: Confirm the STEM supply fan repair status and obtain a timeline for controls-related work.
· Operations/Facilities Management: Continue monitoring HVAC concerns in affected buildings.
· Koue: Obtain outstanding phone system updates from Minh and distribute them.
· Koue/Operations Council: Discuss alternative parking, lighting concerns, and closure communications on October 27.
· Koue: Raise website communication needs at Cabinet on October 20 and coordinate with PIO.
· Erika: Obtain a repair update for the Administration Building women’s restroom stall.
· Academic Senate: Coordinate a proposed Davies Hall celebration date.

2

